## Nashik_DG 39
Increase in fuel cost for FY.2022-23 on account of each reason
SN | Reasons | Unit-03 | Unit-04 | Unit-05 | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | WET COAL PROBLEM | 3899.44 | 1753.43 | 2293 | 7945.87 | 3.1431 | 0.1461 | 36.9349
2 | POOR COAL RECEIPT | 0 | 66 | 206.87 | 272.87 | 0.10794 | 0.0050172 | 1.2684
3 | POOR COAL QUALITY | 36 | 108 | 126 | 270 | 0.1068 | 0.0049645 | 1.255
4 | System Problem | 62 | 0 | 2 | 64 | 0.025316 | 0.0011768 | 0.29749
5 | BOILER TUBE LEAKAGE | 364 | 49 | 230 | 643 | 0.25435 | 0.011823 | 2.9889
6 | ID FAN PROBLEM | 95 | 245 | 183 | 523 | 0.20688 | 0.0096164 | 2.4311
7 | CHP PROBLEM | 36 | 112 | 95 | 243 | 0.096121 | 0.004468 | 1.1295
8 | T&IC PROBLEM | 106 | 0 | 75 | 181 | 0.071597 | 0.003328 | 0.84134
9 | PRESSURE PART LEAKAGE | 0 | 69 | 93 | 162 | 0.064081 | 0.0029787 | 0.75303
10 | ELECTRICAL PROBLEM | 66.93 | 0 | 60 | 126.93 | 0.050209 | 0.0023338 | 0.59001
11 | TURBINE VIB./ECCEN. | 113 | 0 | 3 | 116 | 0.045885 | 0.0021329 | 0.5392
12 | PA FAN MOTOR | 107 | 7 | 0 | 114 | 0.045094 | 0.0020961 | 0.52991
13 | TURBINE AUXILLARIES PROBLEM | 46 | 0 | 59 | 105 | 0.041534 | 0.0019306 | 0.48807
14 | GOVERNING PROBLEM | 105 | 0 | 0 | 105 | 0.041534 | 0.0019306 | 0.48807
15 | BUNKER NECK CHOKE UP | 57 | 4 | 18 | 79 | 0.031249 | 0.0014526 | 0.36722
16 | CONDENSOR TUBE LEAKAGE | 0 | 79 | 0 | 79 | 0.031249 | 0.0014526 | 0.36722
17 | Start-Up Withdrawl | 61 | 2 | 2 | 65 | 0.025711 | 0.0011951 | 0.30214
18 | SHEAR PIN FAILURE | 13 | 29 | 13 | 55 | 0.021756 | 0.0010113 | 0.25566
19 | BOTTOM ASH EXTRACTOR PROBLEM | 0 | 31 | 23 | 54 | 0.02136 | 0.00099289 | 0.25101
20 | BOILER VALIDITY | 0 | 51 | 0 | 51 | 0.020174 | 0.00093773 | 0.23706
21 | ID FAN MOTOR | 0 | 0 | 47 | 47 | 0.018591 | 0.00086418 | 0.21847
22 | TOLLING OF MAHAGENCO COAL TO IPP CASE-IV | 0 | 0 | 43 | 43 | 0.017009 | 0.00079064 | 0.19988
23 | FLAME FAILURE | 0 | 0 | 36 | 36 | 0.01424 | 0.00066193 | 0.16734
24 | HYDROGEN LEAKAGE | 35 | 0 | 0 | 35 | 0.013845 | 0.00064354 | 0.16269
25 | BFP PROBLEM | 15 | 5 | 13 | 33 | 0.013054 | 0.00060677 | 0.15339
26 | Coal Cycle Problem | 1 | 16 | 6 | 23 | 0.0090979 | 0.0004229 | 0.10691
27 | BOILER AUXILLARIES PROBLEM | 0 | 0 | 12 | 12 | 0.0047467 | 0.00022064 | 0.05578
28 | AIR PREHEATER PROBLEM | 8 | 0 | 0 | 8 | 0.0031645 | 0.0001471 | 0.037186
29 | FLAME STABILITY AT 55 PERCENT LOADING | 0 | 6 | 0 | 6 | 0.0023734 | 0.00011032 | 0.02789
30 | DURING BOTTOM ASH EVACUATION | 0 | 0 | 4 | 4 | 0.0015822 | 7.3548e-05 | 0.018593
31 | C.T.FAN PROBLEM | 0 | 2 | 0 | 2 | 0.00079112 | 3.6774e-05 | 0.0092966
32 | ASH DISPOSAL SYS PROBLEM | 2 | 0 | 0 | 2 | 0.00079112 | 3.6774e-05 | 0.0092966
33 | GUN TRIAL | 1 | 0 | 0 | 1 | 0.00039556 | 1.8387e-05 | 0.0046483
34 | HT MOTOR PROBLEM | 1 | 0 | 0 | 1 | 0.00039556 | 1.8387e-05 | 0.0046483
| TOTAL | 5230.37 | 2634.43 | 3642.87 | 11507.67 | 4.552 | 0.21159 | 53.4912
Calculations
1 | Actual Generation | Mus | 2528.056
2 | Normative Oil Consumption | ml/kwh | 1
3 | Actual Oil Consumption | Kl | 11507.67
4 | Normative Oil Consumption | Kl | 2528.056
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 8979.614
6 | Oil Cost for FY.22-23 | Rs. Kl | 59569.644
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 53.4912
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.21159

## Nashik_DG 67
Increase in fuel cost for FY.2023-24 on account of each reason
SN | Reasons | Unit-03 | Unit-04 | Unit-05 | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | WET COAL PROBLEM | 198 | 70 | 81 | 349 | 0.13183 | 0.0032912 | 0.87131
2 | TOLLING OF MAHAGENCO COAL TO IPP CASE-IV | 134 | 0 | 120 | 254 | 0.095944 | 0.0023953 | 0.63413
3 | POOR COAL QUALITY | 10 | 30 | 21 | 61 | 0.023042 | 0.00057525 | 0.15229
4 | System Problem | 0 | 1 | 5 | 6 | 0.0022664 | 5.6582e-05 | 0.014979
5 | BOILER TUBE LEAKAGE | 761.82 | 244 | 255 | 1260.82 | 0.47625 | 0.01189 | 3.1477
6 | Start-Up Withdrawl | 170.09 | 152 | 78.5 | 400.59 | 0.15132 | 0.0037777 | 1.0001
7 | ID FAN PROBLEM | 70 | 178 | 118 | 366 | 0.13825 | 0.0034515 | 0.91375
8 | SHEAR PIN FAILURE | 64.5 | 49.5 | 86.5 | 200.5 | 0.075735 | 0.0018908 | 0.50056
9 | ELECTRICAL PROBLEM | 0 | 195 | 0 | 195 | 0.073658 | 0.0018389 | 0.48683
10 | CONDENSOR TUBE LEAKAGE | 129 | 37 | 0 | 166 | 0.062704 | 0.0015654 | 0.41443
11 | FLAME FAILURE | 52 | 0 | 103 | 155 | 0.058549 | 0.0014617 | 0.38697
12 | GOVERNING PROBLEM | 119 | 19 | 2 | 140 | 0.052883 | 0.0013203 | 0.34952
13 | BUNKER NECK CHOKE UP | 52 | 12.5 | 74 | 138.5 | 0.052316 | 0.0013061 | 0.34578
14 | PA FAN PROBLEM | 34 | 102 | 0 | 136 | 0.051372 | 0.0012825 | 0.33953
15 | PRESSURE PART LEAKAGE | 0 | 7 | 115 | 122 | 0.046083 | 0.0011505 | 0.30458
16 | TURBINE AUXILLARIES PROBLEM | 113 | 0 | 0 | 113 | 0.042684 | 0.0010656 | 0.28211
17 | ID FAN MOTOR | 0 | 0 | 86 | 86 | 0.032485 | 0.00081101 | 0.21471
18 | BOTTOM ASH EXTRACTOR PROBLEM | 4 | 16 | 40 | 60 | 0.022664 | 0.00056582 | 0.14979
19 | HP HEATERS PROBLEM | 32 | 0 | 27 | 59 | 0.022286 | 0.00055639 | 0.1473
20 | PA FAN MOTOR | 0 | 48 | 0 | 48 | 0.018131 | 0.00045266 | 0.11984
21 | ESP PROBLEM | 43.5 | 0 | 0 | 43.5 | 0.016431 | 0.00041022 | 0.1086
22 | T&IC PROBLEM | 0 | 36 | 0 | 36 | 0.013598 | 0.00033949 | 0.089877
23 | COAL MILL PROBLEMS | 2 | 13 | 17 | 32 | 0.012087 | 0.00030177 | 0.07989
24 | OTHER OPERATIONAL PROBLEMS | 0 | 22 | 0 | 22 | 0.0083101 | 0.00020747 | 0.054925
25 | CLINKER FORMATION | 6 | 10 | 5 | 21 | 0.0079324 | 0.00019804 | 0.052428
26 | COOLING TOWER LIFT PUMP PROBLEM | 0 | 17 | 0 | 17 | 0.0064215 | 0.00016032 | 0.042442
27 | OTHER AUXILLARY PROBLEM | 15 | 2 | 0 | 17 | 0.0064215 | 0.00016032 | 0.042442
28 | ASH DISPOSAL SYS PROBLEM | 0 | 9 | 2 | 11 | 0.0041551 | 0.00010373 | 0.027462
29 | BFP PROBLEM | 0 | 0 | 10 | 10 | 0.0037773 | 9.4304e-05 | 0.024966
30 | CONDENSOR VACUUM PROBLEM | 5.15 | 0 | 3 | 8.15 | 0.0030785 | 7.6858e-05 | 0.020347
31 | CHP PROBLEM | 4 | 1 | 0 | 5 | 0.0018887 | 4.7152e-05 | 0.012483
32 | FD FAN PROBLEM | 0 | 2 | 0 | 2 | 0.00075547 | 1.8861e-05 | 0.0049932
33 | CLINKER GRINDER PROBLEM | 0 | 0 | 2 | 2 | 0.00075547 | 1.8861e-05 | 0.0049932
34 | GUN TRIAL | 0 | 0 | 2 | 2 | 0.00075547 | 1.8861e-05 | 0.0049932
| Total | 2019.06 | 1273 | 1253 | 4545.06 | 1.7168 | 0.042862 | 11.3471
Calculations
1 | Actual Generation | Mus | 2647.376
2 | Normative Oil Consumption | ml/kwh | 1
3 | Actual Oil Consumption | Kl | 4545.06
4 | Normative Oil Consumption | Kl | 2647.376
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 1897.684
6 | Oil Cost for FY.23-24 | Rs. Kl | 59794.4011
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 11.3471
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.042862

## Bhusawal 3_DG 39
Increase in fuel cost for FY.2022-23 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 582 | 0.81339 | 0.035985 | 2.5748
2 | BOILER LIGHT-UP (WARM CONDITION) | 202 | 0.28231 | 0.01249 | 0.89367
3 | UNIT WITHDRAWAL (FORCED OUTAGE) | 8 | 0.011181 | 0.00049464 | 0.035393
4 | FLAME STABILITY | 1483 | 2.0726 | 0.091694 | 6.5609
5 | WET COAL PROBLEM | 611 | 0.85392 | 0.037778 | 2.7031
6 | POOR COAL QUALITY | 162 | 0.22641 | 0.010016 | 0.7167
7 | POOR COAL RECEIPT | 13 | 0.018168 | 0.00080379 | 0.057513
8 | CHP PROBLEM | 208 | 0.2907 | 0.012861 | 0.92021
9 | COAL FEEDER PROBLEMS | 55 | 0.076867 | 0.0034007 | 0.24333
10 | NO COAL FLOW FROM BUNKER | 77 | 0.10761 | 0.0047609 | 0.34066
11 | BUNKER NECK CHOKE UP | 127 | 0.17749 | 0.0078524 | 0.56186
12 | COAL MILL PROBLEMS | 4 | 0.0055903 | 0.00024732 | 0.017696
13 | GOVERNING PROBLEM | 5 | 0.0069879 | 0.00030915 | 0.022121
14 | FOREIGN MATERIAL IN C/M | 107 | 0.14954 | 0.0066158 | 0.47338
15 | SHEAR PIN FAILURE | 1 | 0.0013976 | 6.183e-05 | 0.0044241
16 | SET STABILISATION | 339 | 0.47378 | 0.02096 | 1.4998
17 | UNIT STARTUP | 117 | 0.16352 | 0.0072341 | 0.51762
18 | ASH DISPOSAL SYS PROBLEM | 8 | 0.011181 | 0.00049464 | 0.035393
19 | ID FAN MOTOR | 10 | 0.013976 | 0.0006183 | 0.044241
| TOTAL | 4119 | 5.7566 | 0.25468 | 18.2229
Calculations
1 | Actual Generation | Mus | 715.526
2 | Normative Oil Consumption | ml/kwh | 1.4
3 | Actual Oil Consumption | Kl | 4119
4 | Normative Oil Consumption | Kl | 1001.7364
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 3117.2636
6 | Oil Cost for FY.22-23 | Rs. Kl | 58457.9592
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 18.2229
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.25468

## Bhusawal 3_DG 67
Increase in fuel cost for FY.2023-24 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 136 | 0.13385 | 0.004771 | 0.48475
2 | BOILER LIGHT-UP (WARM CONDITION) | 283 | 0.27853 | 0.0099278 | 1.0087
3 | UNIT WITHDRAWAL (FORCED OUTAGE) | 5 | 0.0049211 | 0.0001754 | 0.017822
4 | FLAME STABILITY | 245 | 0.24113 | 0.0085947 | 0.87326
5 | FURNANCE DRAFT | 9 | 0.0088579 | 0.00031572 | 0.032079
6 | WET COAL PROBLEM | 1189 | 1.1702 | 0.041711 | 4.238
7 | POOR COAL QUALITY | 181 | 0.17814 | 0.0063496 | 0.64514
8 | CHP PROBLEM | 54 | 0.053148 | 0.0018943 | 0.19247
9 | CHP BUNKERING PROBLEM | 20 | 0.019684 | 0.00070161 | 0.071286
10 | COAL FEEDER SHEAR PIN FAILURE | 2 | 0.0019684 | 7.0161e-05 | 0.0071286
11 | NO COAL FLOW FROM BUNKER | 22 | 0.021653 | 0.00077177 | 0.078415
12 | COAL MILL PROBLEMS | 71 | 0.069879 | 0.0024907 | 0.25307
13 | ID FAN PROBLEM | 483 | 0.47537 | 0.016944 | 1.7216
14 | BOTTOM ASH EXTRACTOR PROBLEM | 3 | 0.0029526 | 0.00010524 | 0.010693
15 | CLINKER FORMATION | 42 | 0.041337 | 0.0014734 | 0.1497
16 | ESP PROBLEM | 140 | 0.13779 | 0.0049113 | 0.49901
17 | CONDENSOR VACUUM PROBLEM | 3 | 0.0029526 | 0.00010524 | 0.010693
18 | AIR PREHEATER PROBLEM | 8 | 0.0078737 | 0.00028064 | 0.028515
19 | FOREIGN MATERIAL IN C/M | 43 | 0.042321 | 0.0015085 | 0.15327
20 | SET STABILISATION | 276.502 | 0.27214 | 0.0096998 | 0.98554
21 | UNIT STARTUP | 294 | 0.28936 | 0.010314 | 1.0479
22 | FLAME FAILURE | 37 | 0.036416 | 0.001298 | 0.13188
23 | BOILER VALIDITY | 36 | 0.035432 | 0.0012629 | 0.12832
24 | FURNACE PRESSURE VERY LOW | 13 | 0.012795 | 0.00045605 | 0.046336
25 | BOILER PASSIVATION | 70 | 0.068895 | 0.0024556 | 0.2495
| TOTAL | 3665.502 | 3.6076 | 0.12859 | 13.065
Calculations
1 | Actual Generation | Mus | 1016.04
2 | Normative Oil Consumption | ml/kwh | 1.4
3 | Actual Oil Consumption | Kl | 3665.502
4 | Normative Oil Consumption | Kl | 1422.456
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 2243.046
6 | Oil Cost for FY.22-23 | Rs. Kl | 58246.8238
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 13.065
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.12859

## Bhusawal 4-5_DG 39
Increase in fuel cost for FY.2022-23 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 759 | 0.12403 | 0.0054474 | 3.3335
2 | BOILER START UP | 1120 | 0.18302 | 0.0080383 | 4.919
3 | FLAME STABILITY | 5825 | 0.95188 | 0.041806 | 25.5832
4 | WET COAL PROBLEM | 2127 | 0.34758 | 0.015265 | 9.3417
5 | POOR COAL QUALITY | 78 | 0.012746 | 0.00055981 | 0.34257
6 | CHP PROBLEM | 118 | 0.019283 | 0.00084689 | 0.51825
7 | CHP BUNKERING PROBLEM | 111 | 0.018139 | 0.00079665 | 0.48751
8 | COAL FEEDER PROBLEMS | 180 | 0.029414 | 0.0012919 | 0.79055
9 | NO COAL FLOW FROM BUNKER | 351 | 0.057358 | 0.0025191 | 1.5416
10 | COAL MILL PROBLEMS | 179.5 | 0.029333 | 0.0012883 | 0.78836
11 | COAL MILL CHANGEOVER | 19 | 0.0031048 | 0.00013636 | 0.083447
12 | ID FAN PROBLEM | 31 | 0.0050658 | 0.00022249 | 0.13615
13 | CLINKER FORMATION | 20 | 0.0032682 | 0.00014354 | 0.087839
14 | ELECTRICAL PROBLEM | 52 | 0.0084974 | 0.0003732 | 0.22838
15 | GUN TRIAL | 12 | 0.0019609 | 8.6124e-05 | 0.052704
16 | SET STABILISATION | 1075 | 0.17567 | 0.0077153 | 4.7214
17 | STARTUP/WITHDRAWL | 216 | 0.035297 | 0.0015502 | 0.94866
18 | OTHER OPERATIONAL PROBLEMS | 9 | 0.0014707 | 6.4593e-05 | 0.039528
19 | MORE THAN 2 COAL CYC. NOT AVAIL. | 2 | 0.00032682 | 1.4354e-05 | 0.0087839
20 | BOILER PASSIVATION | 94 | 0.015361 | 0.00067464 | 0.41284
21 | FLAME STABILITY AT 55 PERCENT LOADING | 28 | 0.0045755 | 0.00020096 | 0.12297
| TOTAL | 12406.5 | 2.0274 | 0.089042 | 54.4889
Calculations
1 | Actual Generation | Mus | 6119.49
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 12406.5
4 | Normative Oil Consumption | Kl | 3059.745
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 9346.755
6 | Oil Cost for FY.22-23 | Rs. Kl | 58297.1318 |  | 53549.4685 | 10006.5
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 54.4889 |  | 78091.9204 | 2400
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.089042 |  | 58297.1318 | 12406.5

## Bhusawal 4-5_DG 67
Increase in fuel cost for FY.2023-24 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 532 | 0.081108 | 0.0021844 | 1.4328
2 | BOILER START UP | 1031 | 0.15718 | 0.0042333 | 2.7767
3 | FLAME STABILITY | 1997.267 | 0.3045 | 0.0082008 | 5.3791
4 | WET COAL PROBLEM | 215 | 0.032778 | 0.00088279 | 0.57904
5 | POOR COAL QUALITY | 121 | 0.018447 | 0.00049683 | 0.32588
6 | CHP BUNKERING PROBLEM | 194 | 0.029577 | 0.00079657 | 0.52248
7 | COAL FEEDER PROBLEMS | 44 | 0.0067081 | 0.00018067 | 0.1185
8 | NO COAL FLOW FROM BUNKER | 133 | 0.020277 | 0.0005461 | 0.3582
9 | COAL MILL PROBLEMS | 61 | 0.0092999 | 0.00025047 | 0.16429
10 | COAL MILL CHANGEOVER | 16 | 0.0024393 | 6.5696e-05 | 0.043092
11 | BOILER TUBE LEAKAGE | 4 | 0.00060983 | 1.6424e-05 | 0.010773
12 | ID FAN PROBLEM | 20 | 0.0030492 | 8.212e-05 | 0.053864
13 | PA FAN PROBLEM | 906 | 0.13813 | 0.0037201 | 2.4401
14 | T&IC PROBLEM | 4 | 0.00060983 | 1.6424e-05 | 0.010773
15 | TURBINE VIB./ECCEN. | 8 | 0.0012197 | 3.2848e-05 | 0.021546
16 | UNIT STABILIZATION | 90 | 0.013721 | 0.00036954 | 0.24239
17 | SET STABILISATION | 816 | 0.12441 | 0.0033505 | 2.1977
18 | STARTUP/WITHDRAWL | 213 | 0.032473 | 0.00087458 | 0.57366
19 | FLAME FAILURE | 22 | 0.0033541 | 9.0333e-05 | 0.059251
20 | OTHER OPERATIONAL PROBLEMS | 5 | 0.00076229 | 2.053e-05 | 0.013466
| TOTAL | 6432.267 | 0.98065 | 0.026411 | 17.3235
Calculations
1 | Actual Generation | Mus | 6559.195
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 6432.267
4 | Normative Oil Consumption | Kl | 3279.5975
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 3152.6695
6 | Oil Cost for FY.22-23 | Rs. Kl | 54948.7136 |  |  | 5858 | 52289.3036
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 17.3235 |  |  | 574.267 | 82076.9027
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.026411 |  |  | 6432.267 | 54948.7136

## Chandrapur 3-7_DG 39
Increase in fuel cost for FY.2022-23 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | Low sys. demand | 732.75 | 0.087089 | 0.0041874 | 3.5232
2 | System Problem | 0 | 0 | 0 | 0
3 | Water Shortage Problem | 0 | 0 | 0 | 0
4 | PCQ | 0 | 0 | 0 | 0
5 | Wet coal | 24415.58 | 2.9019 | 0.13953 | 117.3951
6 | Poor coal receipt | 201 | 0.023889 | 0.0011487 | 0.96645
7 | Lightup /withdrawl | 9511.358 | 1.1305 | 0.054354 | 45.7326
8 | O/H | 0 | 0 | 0 | 0
9 | Coal mills | 926.382 | 0.1101 | 0.005294 | 4.4542
10 | CHP/ poor bunkering | 203.628 | 0.024202 | 0.0011637 | 0.97909
11 | APH | 299.99 | 0.035655 | 0.0017143 | 1.4424
12 | Pr. Parts | 0 | 0 | 0 | 0
13 | ID / FD /PA fan | 1464.322 | 0.17404 | 0.0083681 | 7.0408
14 | Electrical problem | 45 | 0.0053484 | 0.00025716 | 0.21637
15 | Turbine CV/Brg. problem | 0 | 0 | 0 | 0
16 | Boiler Tube leakage | 0 | 0 | 0 | 0
17 | BFP Problem | 0 | 0 | 0 | 0
18 | Flame stablility | 2133.27 | 0.25354 | 0.012191 | 10.2572
19 | TIC problem | 106 | 0.012598 | 0.00060576 | 0.50967
20 | Passivation | 0 | 0 | 0 | 0
| TOTAL | 40039.28 | 4.7588 | 0.22881 | 192.5171
Calculations
1 | Actual Generation | Mus | 8413.773
2 | Normative Oil Consumption | ml/kwh | 1
3 | Actual Oil Consumption | Kl | 40039.28
4 | Normative Oil Consumption | Kl | 8413.773
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 31625.507 |  |  |  | Rate | Consumption
6 | Oil Cost for FY.22-23 | Rs. Kl | 60873.9814 |  |  | FO | 58734.0387 | 34010.34
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 192.5171 |  |  | LDO | 72947.6671 | 6028
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.22881 |  |  | Total | 60873.9814 | 40038.34

## Chandrapur 3-7_DG 67
Increase in fuel cost for FY.2023-24 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | Low sys. demand | 0 | 0 | 0 | 0
2 | System Problem | 18 | 0.0019913 | 5.9104e-05 | 0.053425
3 | Water Shortage Problem | 194 | 0.021462 | 0.00063701 | 0.5758
4 | PCQ | 0 | 0 | 0 | 0
5 | Wet coal | 7046.72 | 0.77958 | 0.023138 | 20.9149
6 | Poor coal receipt | 0 | 0 | 0 | 0
7 | Lightup /withdrawl | 7188.918 | 0.79531 | 0.023605 | 21.337
8 | O/H | 0 | 0 | 0 | 0
9 | Coal mills | 815.54 | 0.090223 | 0.0026779 | 2.4206
10 | CHP/ poor bunkering | 389.4 | 0.043079 | 0.0012786 | 1.1558
11 | APH | 39 | 0.0043146 | 0.00012806 | 0.11575
12 | Pr. Parts | 0 | 0 | 0 | 0
13 | ID / FD /PA fan | 482.65 | 0.053396 | 0.0015848 | 1.4325
14 | Electrical problem | 29 | 0.0032083 | 9.5223e-05 | 0.086073
15 | Turbine CV/Brg. problem | 0 | 0 | 0 | 0
16 | Boiler Tube leakage | 0 | 0 | 0 | 0
17 | BFP Problem | 0 | 0 | 0 | 0
18 | Flame stablility | 1594.822 | 0.17644 | 0.0052367 | 4.7335
19 | TIC problem | 67.4 | 0.0074565 | 0.00022131 | 0.20005
20 | Passivation | 34 | 0.0037614 | 0.00011164 | 0.10091
| TOTAL | 17899.45 | 1.9802 | 0.058774 | 53.1262
Calculations
1 | Actual Generation | Mus | 9039.119
2 | Normative Oil Consumption | ml/kwh | 1
3 | Actual Oil Consumption | Kl | 17899.45
4 | Normative Oil Consumption | Kl | 9039.119
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 8860.331
6 | Oil Cost for FY.22-23 | Rs. Kl | 59959.581 |  |  |  | Rate | Consumption
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 53.1262 |  |  | FO | 53758.2897 | 13225.75
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.058774 |  |  | LDO | 77509.4977 | 4673.34
[6 empty] | Total | 59959.581 | 17899.09

## Chandrapur 8-9_DG 39
Increase in fuel cost for FY.2022-23 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | Low sys. demand | 0 | 0 | 0 | 0
2 | System Problem | 0 | 0 | 0 | 0
3 | Water Shortage Problem | 0 | 0 | 0 | 0
4 | PCQ | 0 | 0 | 0 | 0
5 | Wet coal | 438 | 0.065682 | 0 | 0
6 | Poor coal receipt | 0 | 0 | 0 | 0
7 | Lightup /withdrawl | 1831 | 0.27457 | 0 | 0
8 | O/H | 0 | 0 | 0 | 0
9 | Coal mills | 8 | 0.0011997 | 0 | 0
10 | CHP/ poor bunkering | 0 | 0 | 0 | 0
11 | APH | 0 | 0 | 0 | 0
12 | Pr. Parts | 16 | 0.0023993 | 0 | 0
13 | ID / FD /PA fan | 76 | 0.011397 | 0 | 0
14 | Electrical problem | 0 | 0 | 0 | 0
15 | Turbine CV/Brg. problem | 15 | 0.0022494 | 0 | 0
16 | Boiler Tube leakage | 0 | 0 | 0 | 0
17 | BFP Problem | 14 | 0.0020994 | 0 | 0
18 | Flame stablility | 25 | 0.0037489 | 0 | 0
19 | TIC problem | 0 | 0 | 0 | 0
20 | Passivation | 0 | 0 | 0 | 0
| TOTAL | 2423 | 0.36335 | 0 | 0
Calculations
1 | Actual Generation | Mus | 6668.541
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 2423
4 | Normative Oil Consumption | Kl | 3334.2705
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | -911.2705 |  |  |  | Rate | Consumption
6 | Oil Cost for FY.22-23 | Rs. Kl |  |  |  | FO | 56257.0757 | 1919.5
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 0 |  |  | LDO | 73975.6619 | 503.5
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0 |  |  | Total | 59939.0023 | 2423

## Chandrapur 8-9_DG 67
Increase in fuel cost for FY.2023-24 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | Low sys. demand | 0 | 0 | 0 | 0
2 | System Problem | 0 | 0 | 0 | 0
3 | Water Shortage Problem | 0 | 0 | 0 | 0
4 | PCQ | 0 | 0 | 0 | 0
5 | Wet coal | 267.76 | 0.036981 | -0.0012294 | -0.89016
6 | Poor coal receipt | 0 | 0 | 0 | 0
7 | Lightup /withdrawl | 1513.87 | 0.20908 | -0.0069509 | -5.0328
8 | O/H | 0 | 0 | 0 | 0
9 | Coal mills | 7.5 | 0.0010358 | -3.4436e-05 | -0.024934
10 | CHP/ poor bunkering | 19.4 | 0.0026794 | -8.9074e-05 | -0.064495
11 | APH | 144.29 | 0.019928 | -0.0006625 | -0.47969
12 | Pr. Parts | 0 | 0 | 0 | 0
13 | ID / FD /PA fan | 80 | 0.011049 | -0.00036732 | -0.26596
14 | Electrical problem | 42 | 0.0058007 | -0.00019284 | -0.13963
15 | Turbine CV/Brg. problem | 0 | 0 | 0 | 0
16 | Boiler Tube leakage | 0 | 0 | 0 | 0
17 | BFP Problem | 9 | 0.001243 | -4.1323e-05 | -0.02992
18 | Flame stablility | 175.5 | 0.024238 | -0.0008058 | -0.58344
19 | TIC problem | 35 | 0.0048339 | -0.0001607 | -0.11636
20 | Passivation | 11 | 0.0015192 | -5.0506e-05 | -0.036569
| TOTAL | 2305.32 | 0.31839 | -0.010585 | -7.664
Calculations
1 | Actual Generation | Mus | 7240.55
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 2305.32
4 | Normative Oil Consumption | Kl | 3620.275
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | -1314.955
6 | Oil Cost for FY.22-23 | Rs. Kl | 58283.0653 |  |  |  | Rate | Consumption
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | -7.664 |  |  | FO | 54314.2309 | 1919.63
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | -0.010585 |  |  | LDO | 78020.6133 | 386
[6 empty] | Total | 58283.0653 | 2305.63

## Kpkd 1-4_DG 39
Increase in fuel cost for FY.2022-23 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 622 | 0.14343 | 0.0064955 | 2.8169
2 | BOILER LIGHT-UP (WARM CONDITION) | 2217.5 | 0.51134 | 0.023157 | 10.0424
3 | FLAME STABILITY | 2441.5 | 0.563 | 0.025497 | 11.0569
4 | WET COAL PROBLEM | 3613 | 0.83314 | 0.037731 | 16.3622
5 | POOR COAL QUALITY | 45 | 0.010377 | 0.00046993 | 0.20379
6 | POOR COAL RECEIPT | 1272 | 0.29332 | 0.013283 | 5.7605
7 | CHP PROBLEM | 93 | 0.021445 | 0.0009712 | 0.42117
8 | CHP BUNKERING PROBLEM | 1064 | 0.24535 | 0.011111 | 4.8186
9 | COAL FEEDER PROBLEMS | 204 | 0.047041 | 0.0021304 | 0.92386
10 | COAL FEEDER SHEAR PIN FAILURE | 38 | 0.0087626 | 0.00039683 | 0.17209
11 | NO COAL FLOW FROM BUNKER | 118.5 | 0.027326 | 0.0012375 | 0.53665
12 | BUNKER NECK CHOKE UP | 125 | 0.028824 | 0.0013054 | 0.56609
13 | COAL MILL PROBLEMS | 4167.024 | 0.9609 | 0.043516 | 18.8713
14 | DURING SOOT BLOWING | 20 | 0.0046119 | 0.00020886 | 0.090574
15 | ID FAN PROBLEM | 1440 | 0.33206 | 0.015038 | 6.5213
16 | FD FAN PROBLEM | 94 | 0.021676 | 0.00098164 | 0.4257
17 | PA FAN PROBLEM | 360 | 0.083014 | 0.0037595 | 1.6303
18 | CLINKER FORMATION | 23 | 0.0053037 | 0.00024019 | 0.10416
19 | OTHER AUXILLARY PROBLEM | 36 | 0.0083014 | 0.00037595 | 0.16303
20 | ELECTRICAL PROBLEM | 30 | 0.0069179 | 0.00031329 | 0.13586
21 | BFP PROBLEM | 2 | 0.00046119 | 2.0886e-05 | 0.0090574
22 | AIR PREHEATER PROBLEM | 2 | 0.00046119 | 2.0886e-05 | 0.0090574
23 | FOREIGN MATERIAL IN C/M | 14 | 0.0032283 | 0.0001462 | 0.063402
24 | FLAME SCANNERS FLICKERING | 61 | 0.014066 | 0.00063702 | 0.27625
25 | GUN TRIAL | 2 | 0.00046119 | 2.0886e-05 | 0.0090574
26 | UNIT STABILIZATION | 2 | 0.00046119 | 2.0886e-05 | 0.0090574
27 | SHEAR PIN FAILURE | 400 | 0.092238 | 0.0041772 | 1.8115
28 | SET STABILISATION | 684 | 0.15773 | 0.007143 | 3.0976
29 | UNIT STARTUP | 90 | 0.020754 | 0.00093987 | 0.40758
30 | COAL CYCLE PROBLEM | 1802.581 | 0.41567 | 0.018824 | 8.1634
31 | MORE THAN 2 COAL CYC. NOT AVAIL. | 24 | 0.0055343 | 0.00025063 | 0.10869
32 | BOILER PASSIVATION | 134 | 0.0309 | 0.0013994 | 0.60685
33 | FLAME STABILITY AT 55 PERCENT LOADING | 5 | 0.001153 | 5.2215e-05 | 0.022644
34 | ID FAN MOTOR | 14 | 0.0032283 | 0.0001462 | 0.063402
35 | FD FAN MOTOR | 32 | 0.007379 | 0.00033418 | 0.14492
| TOTAL | 21292.105 | 4.9099 | 0.22235 | 96.4258
Calculations
1 | Actual Generation | Mus | 4336.604
2 | Normative Oil Consumption | ml/kwh | 1.2
3 | Actual Oil Consumption | Kl | 21292.105
4 | Normative Oil Consumption | Kl | 5203.9248
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 16088.1802 |  |  |  | Rate | Consumption
6 | Oil Cost for FY.22-23 | Rs. Kl | 59935.8263 |  |  | FO | 59339.1315 | 20068.605
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 96.4258 |  |  | LDO | 69723.1843 | 1223.5
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.22235 |  |  | Total | 59935.8263 | 21292.105

## Kpkd 1-4_DG 67
Increase in fuel cost for FY.2023-24 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 433 | 0.092594 | 0.0026805 | 1.2535
2 | BOILER LIGHT-UP (WARM CONDITION) | 2438 | 0.52135 | 0.015092 | 7.0576
3 | UNIT WITHDRAWAL (PLANNED OUTAGE) | 8 | 0.0017108 | 4.9524e-05 | 0.023159
4 | FLAME STABILITY | 179.5 | 0.038385 | 0.0011112 | 0.51962
5 | WET COAL PROBLEM | 493 | 0.10543 | 0.0030519 | 1.4272
6 | POOR COAL QUALITY | 110 | 0.023523 | 0.00068095 | 0.31843
7 | CHP PROBLEM | 29 | 0.0062015 | 0.00017952 | 0.083951
8 | CHP BUNKERING PROBLEM | 1220.5 | 0.261 | 0.0075555 | 3.5332
9 | COAL FEEDER PROBLEMS | 74 | 0.015824 | 0.00045809 | 0.21422
10 | COAL FEEDER SHEAR PIN FAILURE | 43.17 | 0.0092316 | 0.00026724 | 0.12497
11 | NO COAL FLOW FROM BUNKER | 497.5 | 0.10639 | 0.0030798 | 1.4402
12 | BUNKER NECK CHOKE UP | 61 | 0.013044 | 0.00037762 | 0.17659
13 | COAL MILL PROBLEMS | 2477.5 | 0.5298 | 0.015337 | 7.172
14 | DURING BOTTOM ASH EVACUATION | 2 | 0.00042769 | 1.2381e-05 | 0.0057897
15 | COAL MILL CHANGEOVER | 1 | 0.00021384 | 6.1905e-06 | 0.0028948
16 | DURING SOOT BLOWING | 8 | 0.0017108 | 4.9524e-05 | 0.023159
17 | PRESSURE PART LEAKAGE | 20 | 0.0042769 | 0.00012381 | 0.057897
18 | TRANSMISSION SYSTEM PROBLEM | 14 | 0.0029938 | 8.6666e-05 | 0.040528
19 | ID FAN PROBLEM | 1590 | 0.34001 | 0.0098428 | 4.6028
20 | PA FAN PROBLEM | 178.5 | 0.038171 | 0.001105 | 0.51673
21 | BOTTOM ASH EXTRACTOR PROBLEM | 15 | 0.0032077 | 9.2857e-05 | 0.043423
22 | CLINKER FORMATION | 80 | 0.017108 | 0.00049524 | 0.23159
23 | OTHER AUXILLARY PROBLEM | 35 | 0.0074845 | 0.00021667 | 0.10132
24 | DRUM LEVEL PROBLEM | 19 | 0.004063 | 0.00011762 | 0.055002
25 | TURBINE VIB./ECCEN. | 10 | 0.0021384 | 6.1905e-05 | 0.028948
26 | FOREIGN MATERIAL IN C/M | 15 | 0.0032077 | 9.2857e-05 | 0.043423
27 | UPPER REJECT GATE CHOKE UP | 1 | 0.00021384 | 6.1905e-06 | 0.0028948
28 | LOWER REJECT GATE CHOKE UP | 6 | 0.0012831 | 3.7143e-05 | 0.017369
29 | FLAME SCANNERS FLICKERING | 67 | 0.014328 | 0.00041476 | 0.19395
30 | UNIT STABILIZATION | 16 | 0.0034215 | 9.9047e-05 | 0.046318
31 | SHEAR PIN FAILURE | 303 | 0.064795 | 0.0018757 | 0.87714
32 | SET STABILISATION | 305 | 0.065222 | 0.0018881 | 0.88293
33 | UNIT STARTUP | 70 | 0.014969 | 0.00043333 | 0.20264
34 | COAL CYCLE PROBLEM | 499 | 0.10671 | 0.003089 | 1.4445
35 | MORE THAN 2 COAL CYC. NOT AVAIL. | 10 | 0.0021384 | 6.1905e-05 | 0.028948
36 | BOILER PASSIVATION | 105 | 0.022454 | 0.00065 | 0.30396
37 | ASH DISPOSAL SYS PROBLEM | 0 | 0 | 0 | 0
38 | ID FAN MOTOR | 413 | 0.088318 | 0.0025567 | 1.1956
39 | FD FAN MOTOR | 0 | 0 | 0 | 0
40 | PA FAN MOTOR | 3 | 0.00064153 | 1.8571e-05 | 0.0086845
| TOTAL | 11849.67 | 2.534 | 0.073355 | 34.303
Calculations
1 | Actual Generation | Mus | 4676.305
2 | Normative Oil Consumption | ml/kwh | 1.2
3 | Actual Oil Consumption | Kl | 11849.67
4 | Normative Oil Consumption | Kl | 5611.566
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 6238.104
6 | Oil Cost for FY.22-23 | Rs. Kl | 54989.4093 |  |  |  | Rate | Consumption
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 34.303 |  |  | FO | 53711.1048 | 11164.67
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.073355 |  |  | LDO | 75824.2237 | 685
[6 empty] | Total | 54989.4093 | 11849.67

## Kpkd 5_DG 39
Increase in fuel cost for FY.2022-23 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 20.02 | 0.005822 | -0.00016177 | -0.055629
2 | BOILER LIGHT-UP (WARM CONDITION) | 510.94 | 0.14859 | -0.0041287 | -1.4197
3 | FLAME STABILITY | 123.4 | 0.035886 | -0.00099715 | -0.34289
4 | WET COAL PROBLEM | 66.4 | 0.01931 | -0.00053655 | -0.1845
5 | POOR COAL QUALITY | 0 | 0 | 0 | 0
6 | POOR COAL RECEIPT | 0 | 0 | 0 | 0
7 | CHP PROBLEM | 0 | 0 | 0 | 0
8 | CHP BUNKERING PROBLEM | 240.56 | 0.069957 | -0.0019439 | -0.66844
9 | COAL FEEDER PROBLEMS | 0 | 0 | 0 | 0
10 | COAL FEEDER SHEAR PIN FAILURE | 0 | 0 | 0 | 0
11 | NO COAL FLOW FROM BUNKER | 0 | 0 | 0 | 0
12 | BUNKER NECK CHOKE UP | 0 | 0 | 0 | 0
13 | COAL MILL PROBLEMS | 0 | 0 | 0 | 0
14 | DURING SOOT BLOWING | 0 | 0 | 0 | 0
15 | ID FAN PROBLEM | 0 | 0 | 0 | 0
16 | FD FAN PROBLEM | 0 | 0 | 0 | 0
17 | PA FAN PROBLEM | 38.78 | 0.011278 | -0.00031337 | -0.10776
18 | CLINKER FORMATION | 0 | 0 | 0 | 0
19 | OTHER AUXILLARY PROBLEM | 0 | 0 | 0 | 0
20 | ELECTRICAL PROBLEM | 0 | 0 | 0 | 0
21 | BFP PROBLEM | 0 | 0 | 0 | 0
22 | AIR PREHEATER PROBLEM | 0 | 0 | 0 | 0
23 | FOREIGN MATERIAL IN C/M | 0 | 0 | 0 | 0
24 | FLAME SCANNERS FLICKERING | 0 | 0 | 0 | 0
25 | GUN TRIAL | 0 | 0 | 0 | 0
26 | UNIT STABILIZATION | 0 | 0 | 0 | 0
27 | SHEAR PIN FAILURE | 0 | 0 | 0 | 0
28 | SET STABILISATION | 181.34 | 0.052735 | -0.0014653 | -0.50389
29 | UNIT STARTUP | 0 | 0 | 0 | 0
30 | COAL CYCLE PROBLEM | 0 | 0 | 0 | 0
31 | MORE THAN 2 COAL CYC. NOT AVAIL. | 0 | 0 | 0 | 0
32 | BOILER PASSIVATION | 0 | 0 | 0 | 0
33 | FLAME STABILITY AT 55 PERCENT LOADING | 0 | 0 | 0 | 0
34 | ID FAN MOTOR | 0 | 0 | 0 | 0
35 | FD FAN MOTOR | 0 | 0 | 0 | 0
| TOTAL | 1181.44 | 0.34357 | -0.0095468 | -3.2829
Calculations
1 | Actual Generation | Mus | 3438.702
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 1181.44
4 | Normative Oil Consumption | Kl | 1719.351
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | -537.911 |  |  |  | Rate | Consumption
6 | Oil Cost for FY.22-23 | Rs. Kl | 61029.6691 |  |  | FO | 59339.1315 | 989.1
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | -3.2829 |  |  | LDO | 69723.1843 | 192.34
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | -0.0095468 |  |  | Total | 61029.6691 | 1181.44

## Kpkd 5_DG 67
Increase in fuel cost for FY.2023-24 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 345.3 | 0.096154 | -0.0024872 | -0.8932
2 | BOILER LIGHT-UP (WARM CONDITION) | 388.46 | 0.10817 | -0.0027981 | -1.0048
3 | UNIT WITHDRAWAL (PLANNED OUTAGE) | 0 | 0 | 0 | 0
4 | FLAME STABILITY | 131.22 | 0.03654 | -0.0009452 | -0.33943
5 | WET COAL PROBLEM | 0 | 0 | 0 | 0
6 | POOR COAL QUALITY | 0 | 0 | 0 | 0
7 | CHP PROBLEM | 0 | 0 | 0 | 0
8 | CHP BUNKERING PROBLEM | 0 | 0 | 0 | 0
9 | COAL FEEDER PROBLEMS | 10 | 0.0027847 | -7.2032e-05 | -0.025867
10 | COAL FEEDER SHEAR PIN FAILURE | 0 | 0 | 0 | 0
11 | NO COAL FLOW FROM BUNKER | 0 | 0 | 0 | 0
12 | BUNKER NECK CHOKE UP | 0 | 0 | 0 | 0
13 | COAL MILL PROBLEMS | 0 | 0 | 0 | 0
14 | DURING BOTTOM ASH EVACUATION | 0 | 0 | 0 | 0
15 | COAL MILL CHANGEOVER | 0 | 0 | 0 | 0
16 | DURING SOOT BLOWING | 0 | 0 | 0 | 0
17 | PRESSURE PART LEAKAGE | 0 | 0 | 0 | 0
18 | TRANSMISSION SYSTEM PROBLEM | 0 | 0 | 0 | 0
19 | ID FAN PROBLEM | 0 | 0 | 0 | 0
20 | PA FAN PROBLEM | 0 | 0 | 0 | 0
21 | BOTTOM ASH EXTRACTOR PROBLEM | 0 | 0 | 0 | 0
22 | CLINKER FORMATION | 9.1 | 0.002534 | -6.5549e-05 | -0.023539
23 | OTHER AUXILLARY PROBLEM | 0 | 0 | 0 | 0
24 | DRUM LEVEL PROBLEM | 0 | 0 | 0 | 0
25 | TURBINE VIB./ECCEN. | 0 | 0 | 0 | 0
26 | FOREIGN MATERIAL IN C/M | 0 | 0 | 0 | 0
27 | UPPER REJECT GATE CHOKE UP | 0 | 0 | 0 | 0
28 | LOWER REJECT GATE CHOKE UP | 0 | 0 | 0 | 0
29 | FLAME SCANNERS FLICKERING | 0 | 0 | 0 | 0
30 | UNIT STABILIZATION | 0 | 0 | 0 | 0
31 | SHEAR PIN FAILURE | 0 | 0 | 0 | 0
32 | SET STABILISATION | 309.82 | 0.086274 | -0.0022317 | -0.80142
33 | UNIT STARTUP | 37.62 | 0.010476 | -0.00027098 | -0.097313
34 | COAL CYCLE PROBLEM | 0 | 0 | 0 | 0
35 | MORE THAN 2 COAL CYC. NOT AVAIL. | 0 | 0 | 0 | 0
36 | BOILER PASSIVATION | 0 | 0 | 0 | 0
37 | ASH DISPOSAL SYS PROBLEM | 10.34 | 0.0028793 | -7.4481e-05 | -0.026747
38 | ID FAN MOTOR | 0 | 0 | 0 | 0
39 | FD FAN MOTOR | 7.68 | 0.0021386 | -5.532e-05 | -0.019866
40 | PA FAN MOTOR | 0 | 0 | 0 | 0
| TOTAL | 1249.54 | 0.34795 | -0.0090006 | -3.2322
Calculations
1 | Actual Generation | Mus | 3591.104
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 1249.54
4 | Normative Oil Consumption | Kl | 1795.552
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | -546.012
6 | Oil Cost for FY.22-23 | Rs. Kl | 59196.8798 |  |  |  | Rate | Consumption
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | -3.2322 |  |  | FO | 53731.872 | 940.44
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | -0.0090006 |  |  | LDO | 75824.2237 | 309.1
[6 empty] | Total | 59196.8798 | 1249.54

## Paras_DG 39
Increase in fuel cost for FY.2022-23 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 76.93 | 0.025061 | 0.001092 | 0.3352
2 | BOILER LIGHT-UP (WARM CONDITION) | 1286.266 | 0.41902 | 0.018258 | 5.6046
3 | UNIT WITHDRAWAL (PLANNED OUTAGE) | 7.693 | 0.0025061 | 0.0001092 | 0.03352
4 | FLAME STABILITY | 212.559 | 0.069245 | 0.0030172 | 0.92617
5 | WET COAL PROBLEM | 531.598 | 0.17318 | 0.0075457 | 2.3163
6 | CHP PROBLEM | 53.061 | 0.017286 | 0.00075317 | 0.2312
7 | CHP BUNKERING PROBLEM | 524.706 | 0.17093 | 0.0074479 | 2.2863
8 | COAL FEEDER PROBLEMS | 159.782 | 0.052052 | 0.002268 | 0.69621
9 | NO COAL FLOW FROM BUNKER | 127.858 | 0.041652 | 0.0018149 | 0.55711
10 | BUNKER NECK CHOKE UP | 5.386 | 0.0017546 | 7.6451e-05 | 0.023468
11 | COAL MILL PROBLEMS | 1252.041 | 0.40787 | 0.017772 | 5.4554
12 | DURING BOTTOM ASH EVACUATION | 30.81 | 0.010037 | 0.00043733 | 0.13425
13 | COAL MILL CHANGEOVER | 4.077 | 0.0013282 | 5.7871e-05 | 0.017764
14 | DURING SOOT BLOWING | 21.543 | 0.007018 | 0.00030579 | 0.093868
15 | ID FAN PROBLEM | 20.002 | 0.006516 | 0.00028392 | 0.087154
16 | FD FAN PROBLEM | 18.463 | 0.0060146 | 0.00026207 | 0.080448
17 | PA FAN PROBLEM | 12.232 | 0.0039848 | 0.00017363 | 0.053298
18 | CLINKER FORMATION | 72.314 | 0.023558 | 0.0010265 | 0.31509
19 | ELECTRICAL PROBLEM | 177.808 | 0.057924 | 0.0025239 | 0.77475
20 | T&IC PROBLEM | 68.467 | 0.022304 | 0.00097185 | 0.29833
21 | TURBINE VIB./ECCEN. | 98.471 | 0.032079 | 0.0013977 | 0.42906
22 | GUN TRIAL | 1.539 | 0.00050136 | 2.1845e-05 | 0.0067058
23 | SET STABILISATION | 465.696 | 0.15171 | 0.0066103 | 2.0291
24 | UNIT STARTUP | 6.549 | 0.0021334 | 9.2959e-05 | 0.028536
25 | HT MOTOR PROBLEM | 36.926 | 0.012029 | 0.00052414 | 0.1609
26 | BOILER VALIDITY | 6.155 | 0.0020051 | 8.7367e-05 | 0.026819
27 | BOILER PASSIVATION | 72.314 | 0.023558 | 0.0010265 | 0.31509
28 |  |  | 0 | 0 | 0
29 |  |  | 0 | 0 | 0
30 |  |  | 0 | 0 | 0
31 |  |  | 0 | 0 | 0
32 |  |  | 0 | 0 | 0
33 |  |  | 0 | 0 | 0
34 |  |  | 0 | 0 | 0
35 |  |  | 0 | 0 | 0
| TOTAL | 5351.246 | 1.7433 | 0.075958 | 23.3167
Calculations
1 | Actual Generation | Mus | 3069.679
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 5351.246
4 | Normative Oil Consumption | Kl | 1534.8395
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 3816.4065 |  |  |  | Rate | Consumption
6 | Oil Cost for FY.22-23 | Rs. Kl | 61095.8728 |  |  | FO | 59997.45 | 4771.506
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 23.3167 |  |  | LDO | 70136.3576 | 579.74
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.075958 |  |  | Total | 61095.8728 | 5351.246

## Paras_DG 67
Increase in fuel cost for FY.2023-24 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) |  | 0 | 0 | 0
2 | BOILER LIGHT-UP (WARM CONDITION) |  | 0 | 0 | 0
3 | UNIT WITHDRAWAL (PLANNED OUTAGE) |  | 0 | 0 | 0
4 | FLAME STABILITY |  | 0 | 0 | 0
5 | WET COAL PROBLEM |  | 0 | 0 | 0
6 | POOR COAL QUALITY |  | 0 | 0 | 0
7 | CHP PROBLEM |  | 0 | 0 | 0
8 | CHP BUNKERING PROBLEM |  | 0 | 0 | 0
9 | COAL FEEDER PROBLEMS |  | 0 | 0 | 0
10 | COAL FEEDER SHEAR PIN FAILURE |  | 0 | 0 | 0
11 | NO COAL FLOW FROM BUNKER |  | 0 | 0 | 0
12 | BUNKER NECK CHOKE UP |  | 0 | 0 | 0
13 | COAL MILL PROBLEMS |  | 0 | 0 | 0
14 | DURING BOTTOM ASH EVACUATION |  | 0 | 0 | 0
15 | COAL MILL CHANGEOVER |  | 0 | 0 | 0
16 | DURING SOOT BLOWING |  | 0 | 0 | 0
17 | PRESSURE PART LEAKAGE |  | 0 | 0 | 0
18 | TRANSMISSION SYSTEM PROBLEM |  | 0 | 0 | 0
19 | ID FAN PROBLEM |  | 0 | 0 | 0
20 | PA FAN PROBLEM |  | 0 | 0 | 0
21 | BOTTOM ASH EXTRACTOR PROBLEM |  | 0 | 0 | 0
22 | CLINKER FORMATION |  | 0 | 0 | 0
23 | OTHER AUXILLARY PROBLEM |  | 0 | 0 | 0
24 | DRUM LEVEL PROBLEM |  | 0 | 0 | 0
25 | TURBINE VIB./ECCEN. |  | 0 | 0 | 0
26 | FOREIGN MATERIAL IN C/M |  | 0 | 0 | 0
27 | UPPER REJECT GATE CHOKE UP |  | 0 | 0 | 0
28 | LOWER REJECT GATE CHOKE UP |  | 0 | 0 | 0
29 | FLAME SCANNERS FLICKERING |  | 0 | 0 | 0
30 | UNIT STABILIZATION |  | 0 | 0 | 0
31 | SHEAR PIN FAILURE |  | 0 | 0 | 0
32 | SET STABILISATION |  | 0 | 0 | 0
33 | UNIT STARTUP |  | 0 | 0 | 0
34 | COAL CYCLE PROBLEM |  | 0 | 0 | 0
35 | MORE THAN 2 COAL CYC. NOT AVAIL. |  | 0 | 0 | 0
36 | BOILER PASSIVATION |  | 0 | 0 | 0
37 | ASH DISPOSAL SYS PROBLEM |  | 0 | 0 | 0
38 | ID FAN MOTOR |  | 0 | 0 | 0
39 | FD FAN MOTOR |  | 0 | 0 | 0
40 | PA FAN MOTOR |  | 0 | 0 | 0
| TOTAL | 1712.505 | 0.47623 | 0 | 0
| Total SFOC ml/kwh | 1712.505 | 0.47623 | Normative Achieved
Calculations
1 | Actual Generation | Mus | 3595.983
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 1712.505
4 | Normative Oil Consumption | Kl | 1797.9915
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | -85.4865
6 | Oil Cost for FY.22-23 | Rs. Kl | 56104.9655 |  |  |  | Rate | Consumption
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | -0.47962 |  |  | FO | 54377.873 | 1564.801
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | -0.0013338 |  |  | LDO | 74402.0739 | 147.704
[6 empty] | Total | 56104.9655 | 1712.505

## Parli 6-7_DG 39
Increase in fuel cost for FY.2022-23 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 763 | 0.273 | 0.0133 | 3.7171
2 | BOILER LIGHT-UP (WARM CONDITION) | 778.35 | 0.27849 | 0.013567 | 3.7918
3 | UNIT WITHDRAWAL (PLANNED OUTAGE) | 1.71 | 0.00061184 | 2.9807e-05 | 0.0083305
4 | UNIT WITHDRAWAL (FORCED OUTAGE) | 18 | 0.0064404 | 0.00031375 | 0.087689
5 | FLAME STABILITY | 151.35 | 0.054153 | 0.0026381 | 0.73732
6 | WET COAL PROBLEM | 745 | 0.26656 | 0.012986 | 3.6294
7 | POOR COAL QUALITY | 391.5 | 0.14008 | 0.0068241 | 1.9072
8 | CHP PROBLEM | 64.5 | 0.023078 | 0.0011243 | 0.31422
9 | COAL FEEDER PROBLEMS | 1253.921 | 0.44865 | 0.021857 | 6.1086
10 | NO COAL FLOW FROM BUNKER | 50 | 0.01789 | 0.00087154 | 0.24358
11 | BUNKER NECK CHOKE UP | 155 | 0.055459 | 0.0027018 | 0.7551
12 | COAL MILL PROBLEMS | 3411.444 | 1.2206 | 0.059464 | 16.6193
13 | COAL MILL PURGING | 20 | 0.007156 | 0.00034862 | 0.097433
14 | COAL MILL CHANGEOVER | 74 | 0.026477 | 0.0012899 | 0.3605
15 | DURING SOOT BLOWING | 2 | 0.0007156 | 3.4862e-05 | 0.0097433
16 | BOILER TUBE LEAKAGE | 24 | 0.0085872 | 0.00041834 | 0.11692
17 | ID FAN PROBLEM | 60 | 0.021468 | 0.0010458 | 0.2923
18 | FD FAN PROBLEM | 65 | 0.023257 | 0.001133 | 0.31666
19 | PA FAN PROBLEM | 1369.37 | 0.48996 | 0.023869 | 6.6711
20 | OTHER AUXILLARY PROBLEM | 0 | 0 | 0 | 0
21 | ELECTRICAL PROBLEM | 100 | 0.03578 | 0.0017431 | 0.48716
22 | T&IC PROBLEM | 28 | 0.010018 | 0.00048806 | 0.13641
23 | CONDENSOR VACUUM PROBLEM | 10.6 | 0.0037927 | 0.00018477 | 0.051639
24 | GOVERNING PROBLEM | 7 | 0.0025046 | 0.00012202 | 0.034101
25 | HP HEATERS PROBLEM | 10 | 0.003578 | 0.00017431 | 0.048716
26 | FOREIGN MATERIAL IN C/M | 8 | 0.0028624 | 0.00013945 | 0.038973
27 | FLAME SCANNERS FLICKERING | 30 | 0.010734 | 0.00052292 | 0.14615
28 | GUN TRIAL | 2 | 0.0007156 | 3.4862e-05 | 0.0097433
29 | UNIT STABILIZATION | 95.79 | 0.034274 | 0.0016697 | 0.46665
30 | SET STABILISATION | 431 | 0.15421 | 0.0075127 | 2.0997
31 | UNIT STARTUP | 241 | 0.08623 | 0.0042008 | 1.1741
32 | COAL CYCLE PROBLEM | 7 | 0.0025046 | 0.00012202 | 0.034101
33 | HT MOTOR PROBLEM | 84 | 0.030055 | 0.0014642 | 0.40922
34 | BOILER PASSIVATION | 107.86 | 0.038592 | 0.0018801 | 0.52545
35 | PA FAN MOTOR | 0 | 0 | 0 | 0
| TOTAL | 10560.395 | 3.7785 | 0.18408 | 51.4464
Calculations
1 | Actual Generation | Mus | 2794.847
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 10560.395
4 | Normative Oil Consumption | Kl | 1397.4235
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 9162.9715 |  |  |  | Rate | Consumption
6 | Oil Cost for FY.22-23 | Rs. Kl | 56145.9619 |  |  | FO | 55667.8216 | 9696.085
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 51.4464 |  |  | LDO | 61509.8811 | 864.31
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.18408 |  |  | Total | 56145.9619 | 10560.395

## Parli 6-7_DG 67
Increase in fuel cost for FY.2023-24 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 853.65 | 0.30387 | 0.016041 | 4.5063
2 | BOILER LIGHT-UP (WARM CONDITION) | 684.2 | 0.24355 | 0.012857 | 3.6118
3 | UNIT WITHDRAWAL (PLANNED OUTAGE) | 3.5 | 0.0012459 | 6.5769e-05 | 0.018476
4 | UNIT WITHDRAWAL (FORCED OUTAGE) | 8.5 | 0.0030257 | 0.00015973 | 0.044871
5 | FLAME STABILITY | 88.4 | 0.031468 | 0.0016611 | 0.46665
6 | POOR COAL QUALITY | 0 | 0 | 0 | 0
7 | CHP BUNKERING PROBLEM | 0 | 0 | 0 | 0
8 | COAL FEEDER PROBLEMS | 416.16 | 0.14814 | 0.0078202 | 2.1969
9 | COAL MILL PROBLEMS | 2570.312 | 0.91495 | 0.048299 | 13.5684
10 | COAL MILL PURGING | 0 | 0 | 0 | 0
11 | COAL MILL CHANGEOVER | 68.26 | 0.024299 | 0.0012827 | 0.36034
12 | DURING SOOT BLOWING | 0 | 0 | 0 | 0
13 | BOILER TUBE LEAKAGE | 3.5 | 0.0012459 | 6.5769e-05 | 0.018476
14 | LOW SYSTEM DEMAND-ZERO SCHEDULE | 0 | 0 | 0 | 0
15 | ID FAN PROBLEM | 88.5 | 0.031503 | 0.001663 | 0.46718
16 | FD FAN PROBLEM | 6 | 0.0021358 | 0.00011275 | 0.031673
17 | PA FAN PROBLEM | 83 | 0.029546 | 0.0015597 | 0.43815
18 | ELECTRICAL PROBLEM | 21 | 0.0074754 | 0.00039462 | 0.11086
19 | T&IC PROBLEM | 6.7 | 0.002385 | 0.0001259 | 0.035369
20 | AIR PREHEATER PROBLEM | 0 | 0 | 0 | 0
21 | FLAME SCANNERS FLICKERING | 10.5 | 0.0037377 | 0.00019731 | 0.055428
22 | GUN TRIAL | 14.8 | 0.0052684 | 0.00027811 | 0.078128
23 | UNIT STABILIZATION | 166.17 | 0.059152 | 0.0031225 | 0.87719
24 | SET STABILISATION | 422.61 | 0.15044 | 0.0079414 | 2.2309
25 | UNIT STARTUP | 67.3 | 0.023957 | 0.0012647 | 0.35527
26 | FLAME FAILURE | 113 | 0.040225 | 0.0021234 | 0.59651
27 | OTHER OPERATIONAL PROBLEMS | 7 | 0.0024918 | 0.00013154 | 0.036952
28 | COAL CYCLE PROBLEM | 74 | 0.026342 | 0.0013906 | 0.39064
29 | BOILER PASSIVATION | 0 | 0 | 0 | 0
30 | FD FAN MOTOR | 18 | 0.0064075 | 0.00033824 | 0.09502
| TOTAL | 5795.062 | 2.0629 | 0.1089 | 30.5915
Calculations
1 | Actual Generation | Mus | 2809.225
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 5795.062
4 | Normative Oil Consumption | Kl | 1404.6125
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 4390.4495
6 | Oil Cost for FY.22-23 | Rs. Kl | 69677.3813 |  |  |  | Rate | Consumption
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 30.5915 |  |  | FO | 68526.551 | 4706.862
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.1089 |  |  | LDO | 74655.1422 | 1088.2
[6 empty] | Total | 69677.3813 | 5795.062 | 0

## Parli 8_DG 39
Increase in fuel cost for FY.2022-23 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 570.59 | 0.50355 | 0.025596 | 2.9003
2 | BOILER LIGHT-UP (WARM CONDITION) | 187.82 | 0.16575 | 0.0084253 | 0.9547
3 | UNIT WITHDRAWAL (PLANNED OUTAGE) | 0 | 0 | 0 | 0
4 | UNIT WITHDRAWAL (FORCED OUTAGE) | 62.85 | 0.055466 | 0.0028193 | 0.31947
5 | FLAME STABILITY | 187.06 | 0.16508 | 0.0083912 | 0.95083
6 | WET COAL PROBLEM | 298.52 | 0.26345 | 0.013391 | 1.5174
7 | POOR COAL QUALITY | 22.91 | 0.020218 | 0.0010277 | 0.11645
8 | CHP PROBLEM | 8.18 | 0.0072189 | 0.00036694 | 0.041579
9 | COAL FEEDER PROBLEMS | 194.413 | 0.17157 | 0.0087211 | 0.98821
10 | NO COAL FLOW FROM BUNKER | 0 | 0 | 0 | 0
11 | BUNKER NECK CHOKE UP | 70.48 | 0.062199 | 0.0031616 | 0.35825
12 | COAL MILL PROBLEMS | 3217.306 | 2.8393 | 0.14432 | 16.3537
13 | COAL MILL PURGING | 0 | 0 | 0 | 0
14 | COAL MILL CHANGEOVER | 0 | 0 | 0 | 0
15 | DURING SOOT BLOWING | 7 | 0.0061776 | 0.00031401 | 0.035581
16 | BOILER TUBE LEAKAGE | 0 | 0 | 0 | 0
17 | ID FAN PROBLEM | 14.02 | 0.012373 | 0.00062891 | 0.071264
18 | FD FAN PROBLEM | 146.26 | 0.12908 | 0.006561 | 0.74345
19 | PA FAN PROBLEM | 189.74 | 0.16745 | 0.0085114 | 0.96446
20 | OTHER AUXILLARY PROBLEM | 0 | 0 | 0 | 0
21 | ELECTRICAL PROBLEM | 0 | 0 | 0 | 0
22 | T&IC PROBLEM | 0 | 0 | 0 | 0
23 | CONDENSOR VACUUM PROBLEM | 0 | 0 | 0 | 0
24 | GOVERNING PROBLEM | 0 | 0 | 0 | 0
25 | HP HEATERS PROBLEM | 0 | 0 | 0 | 0
26 | FOREIGN MATERIAL IN C/M | 0 | 0 | 0 | 0
27 | FLAME SCANNERS FLICKERING | 0 | 0 | 0 | 0
28 | GUN TRIAL | 0 | 0 | 0 | 0
29 | UNIT STABILIZATION | 67.242 | 0.059342 | 0.0030164 | 0.34179
30 | SET STABILISATION | 288.73 | 0.25481 | 0.012952 | 1.4676
31 | UNIT STARTUP | 10.78 | 0.0095135 | 0.00048357 | 0.054795
32 | COAL CYCLE PROBLEM | 143.37 | 0.12653 | 0.0064313 | 0.72876
33 | HT MOTOR PROBLEM | 15 | 0.013238 | 0.00067288 | 0.076246
34 | BOILER PASSIVATION | 0 | 0 | 0 | 0
35 | PA FAN MOTOR | 130 | 0.11473 | 0.0058316 | 0.6608
| TOTAL | 5832.271 | 5.147 | 0.26163 | 29.6457
Calculations
1 | Actual Generation | Mus | 1133.131
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 5832.271
4 | Normative Oil Consumption | Kl | 566.5655
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 5265.7055 |  |  |  | Rate | Consumption
6 | Oil Cost for FY.22-23 | Rs. Kl | 56299.5374 |  |  | FO | 55638.4026 | 5175.551
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 29.6457 |  |  | LDO | 61509.8811 | 656.72
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.26163 |  |  | Total | 56299.5374 | 5832.271 | 0

## Parli 8_DG 67
Increase in fuel cost for FY.2023-24 on account of each reason
SN | Reasons | Station | Impact on SOC (ml/kwh) | Increase in Oil Cost due to increase SOC in (Rs/Kwh) | Increase in Oil Cost due to increase SOC in (Rs. Cr.)
1 | BOILER LIGHT-UP (COLD CONDITION) | 382.45 | 0.29533 | 0.01234 | 1.598
2 | BOILER LIGHT-UP (WARM CONDITION) | 170.97 | 0.13202 | 0.0055165 | 0.71438
3 | UNIT WITHDRAWAL (PLANNED OUTAGE) | 0 | 0 | 0 | 0
4 | UNIT WITHDRAWAL (FORCED OUTAGE) | 0 | 0 | 0 | 0
5 | FLAME STABILITY | 28.68 | 0.022147 | 0.00092538 | 0.11984
6 | POOR COAL QUALITY | 2.34 | 0.001807 | 7.5502e-05 | 0.0097774
7 | CHP BUNKERING PROBLEM | 26.84 | 0.020726 | 0.00086601 | 0.11215
8 | COAL FEEDER PROBLEMS | 63.09 | 0.048719 | 0.0020356 | 0.26361
9 | COAL MILL PROBLEMS | 388.12 | 0.29971 | 0.012523 | 1.6217
10 | COAL MILL PURGING | 4.67 | 0.0036062 | 0.00015068 | 0.019513
11 | COAL MILL CHANGEOVER | 8.03 | 0.0062008 | 0.00025909 | 0.033552
12 | DURING SOOT BLOWING | 3.52 | 0.0027182 | 0.00011358 | 0.014708
13 | BOILER TUBE LEAKAGE | 0 | 0 | 0 | 0
14 | LOW SYSTEM DEMAND-ZERO SCHEDULE | 1.16 | 0.00089576 | 3.7428e-05 | 0.0048469
15 | ID FAN PROBLEM | 125.82 | 0.097159 | 0.0040597 | 0.52572
16 | FD FAN PROBLEM | 11.67 | 0.0090117 | 0.00037654 | 0.048762
17 | PA FAN PROBLEM | 0 | 0 | 0 | 0
18 | ELECTRICAL PROBLEM | 0 | 0 | 0 | 0
19 | T&IC PROBLEM | 0 | 0 | 0 | 0
20 | AIR PREHEATER PROBLEM | 1.16 | 0.00089576 | 3.7428e-05 | 0.0048469
21 | FLAME SCANNERS FLICKERING | 0 | 0 | 0 | 0
22 | GUN TRIAL | 0 | 0 | 0 | 0
23 | UNIT STABILIZATION | 46.17 | 0.035653 | 0.0014897 | 0.19292
24 | SET STABILISATION | 205.07 | 0.15836 | 0.0066167 | 0.85686
25 | UNIT STARTUP | 2.33 | 0.0017992 | 7.5179e-05 | 0.0097356
26 | FLAME FAILURE | 0 | 0 | 0 | 0
27 | OTHER OPERATIONAL PROBLEMS | 0 | 0 | 0 | 0
28 | COAL CYCLE PROBLEM | 0 | 0 | 0 | 0
29 | BOILER PASSIVATION | 107 | 0.082626 | 0.0034524 | 0.44709
30 | FD FAN MOTOR | 0 | 0 | 0 | 0
| TOTAL | 1579.09 | 1.2194 | 0.050951 | 6.5981
Calculations
1 | Actual Generation | Mus | 1294.99
2 | Normative Oil Consumption | ml/kwh | 0.5
3 | Actual Oil Consumption | Kl | 1579.09
4 | Normative Oil Consumption | Kl | 647.495
5 | Excess Oil Consumption due to increase in Oil Conumption | Kl | 931.595
6 | Oil Cost for FY.22-23 | Rs. Kl | 70825.3279 |  |  |  | Rate | Consumption
7 | Increase in Oil Cost due to increase SOC | Rs. Cr. | 6.5981 |  |  | FO | 68708.6118 | 1017
8 | Increase in Oil Cost due to increase SOC | Rs/Kwh | 0.050951 |  |  | LDO | 74655.1422 | 562.09
[6 empty] | Total | 70825.3279 | 1579.09